## Sheet1
Hazen-Williams Equation for Pressure Loss in Pipes
Imperial Units
Specified Data
l = length of pipe (ft) | 200
c = Hazen-Williams roughness constant | 140
q = volume flow (gal/min) | 200
dh = inside or hydraulic diameter (inches) | 3
Calculated Pressure Loss
f = friction head loss in feet of water per 100 feet of pipe (ft H20 per 100 ft pipe) | 9.7305
f = friction head loss in psi of water per 100 feet of pipe (psi per 100 ft pipe) | 4.1841
Head loss (ft H20) | 19.461
Head loss (psi) | 8.3682
Calculated Flow Velocity
v = flow velocity (ft/s) | 9.0824
SI Units
Specified Data
l = length of pipe (m) | 30
c = Hazen-Williams roughness constant | 140
q = volume flow (liter/sec) | 10
dh = inside or hydraulic diameter (mm) | 76
Calculated Pressure Loss
f = friction head loss in mm of water per 100 m of pipe (mm H20 per 100 m pipe) | 6406.6173
f = friction head loss in kPa per 100 m of pipe (kPa per 100 m pipe) | 62.8489
Head loss (mm H20) | 1921.9852
Head loss (kPa) | 18.8547
Calculated Flow Velocity
v = flow velocity (m/s) | 2.2044